## Sheet1
Project Name
Name of the Engineering Consultant
Name of the EPC
Applicable 9COM numbers and their respective description/Equipment name
List of Standards applicable for each 9COM number
Number of Systems
Wattage/Load value for each system (if available)
Numbers of sites for each type of system
Required Battery Type
Required Battery Autonomy
Required Battery Capacity
Environmental Conditions
Temperature Range
Support Structure details / specifications
Specifications or details of any other equipment (if available)
Any other service required by the client as part of vendor's scope?
Responses from ChatGPT
Item | Information Extracted from BOQ
Project Name | REPLACE 56" ABQAIQ YANBU PIPELINE (AY-1L) – SECTION 7 – SOLAR POWER SYSTEM
Name of the Engineering Consultant | Worley
Name of the EPC | Bin Quraya Company Limited
Applicable 9COM numbers and their respective description / Equipment name | 6000001239 – Power Supply System: Solar, Photovoltaic, Type Off-Grid including all components & accessories (Non-inspectable)
6000001076 – Battery: Nickel-Cadmium Stationary Storage
6000000859 – Panelboard; Low Voltage, Non-Xproof
List of Standards applicable for each 9COM number | 6000001239 – Solar PV System: SAES-P-128, SAES-P-103, SAES-P-111, SAES-A-112, SAES-P-100, SAES-P-104, SAES-J-902, SAES-M-001
6000001076 – Stationary Batteries: 17-SAMSS-511, SAEP-350
6000000859 – Panelboards: 16-SAMSS-518
Number of Systems | 3 systems (MLIV-1, MLIV-2, MLIV-3)
Wattage / Load value for each system (if available) | NA (Load values not provided in the BOQ)
Numbers of sites for each type of system | MLIV-1 @ KM 3.40 – 1 set
MLIV-2 @ KM 19.40 – 1 set
MLIV-3 @ KM 34.00 – 1 set
Required Battery Type | Nickel-Cadmium Battery (per 17-SAMSS-511)
Required Battery Autonomy | 5 days operation without solar charging
Required Battery Capacity | MLIV-1: 1400 Ah (4 sets) @ C5
MLIV-2: 325 Ah (1 set) @ C5
MLIV-3: 1400 Ah (4 sets) @ C5
Environmental Conditions | Weatherproof, corrosive-resistant, suitable for continuous operation at 56°C ambient, Middle Eastern desert environment
Temperature Range | Up to 56°C effective ambient temperature
Support Structure details / specifications | Hot-dip galvanized per ASTM A123
Designed per 12-SAMSS-007
Withstand 145 km/hr wind speed
Oriented to geographical south (±5°)
Tilt angle optimized for winter solstice
Non-corrosive materials
Specifications or details of any other equipment (if available) | • Charge Controller: Vendor to provide datasheet/catalog
• Fused disconnect combiner between PV array & charge controller
• Array Junction Boxes, Solar Module Junction Boxes
• 24VDC Power Panel (per 16-SAMSS-518)
• Grounding & lightning protection per SAES-P-111
• Solar sizing calculation: Document VE-200705
Any other service required by the client as part of vendor's scope? | • Design, engineering, fabrication, inspection, testing, supply, packing
• Solar system design & assembly
• Installation supervision (if required)
• Commissioning / SAT (if required)
• Training & system support (if required)
• Submission of SPDP per SAEP-31
• Provide datasheets, catalogs, and documentation
• Supply all hardware, software, accessories, and any missing items required for a fully operational system