SUMMARY OF BOQ – OFF-GRID SOLAR POWER SYSTEM (ARAMCO – AY-1L PIPELINE SECTION 7)

1. Required Items, Documents, and Calculations Specified

The BOQ requires the vendor to provide the following documents and engineering deliverables:

- Solar System Sizing Calculation
Document reference: VE-200705 (17 pages)

- Datasheets / Product Catalogs
a) Charge controller datasheets (vendor to provide)
b) Power panels datasheets (references provided in BOQ)
c) Stationary battery datasheets

- Spare Parts Data Package (SPDP) in accordance with SAEP-31, including:
a) Two-year operating spare parts list
b) Capital spare parts list
c) 3 hard copies + 1 soft copy
d) Forms per Appendices B, C, D, E

- Start-up & Commissioning Spare Parts List
Must include manufacturer part numbers, quantities, weights, pricing, etc.

- Foundation design inputs
Vendor must provide:
a) Bearing loads
b) Wind-induced forces
c) Anchor bolt specifications per ARAMCO AA-036322.001 Rev.08

- Engineering Documentation Requirements
a) System design calculations
b) System drawings
c) Structure details
d) Compliance documentation
e) SVL submission for ARAMCO approval (all sub-items must be purchased from ARAMCO-approved sources)

- Inspection & Testing Requirements
As per ARAMCO’s form 175-000003, plus any project-specific testing requirements.

2. Information Given About the Equipment

Solar Power System (24 VDC, Off-Grid)

- Type: Monocrystalline or Polycrystalline PV modules

- Each string must include a Schottky blocking diode

- Fused disconnect combiner required between PV array and charge controller

- Solar array oriented south (±5°) with optimum winter solstice tilt

- Structure must withstand 145 km/hr wind speed

- All structures must be non-corrosive and hot-dip galvanized (ASTM A123)

Charge Controller

- PWM charge controller

- Vendor must submit datasheet/catalog

- Located inside array control center

Array Control Center

Includes:

- Charge controller

- Metering and control circuits

- Wiring and interconnections

- Enclosures

- Combiner junction box

- Solar module junction boxes

Batteries

- Type: Nickel-Cadmium

- Compliance: 17-SAMSS-511

- Battery autonomy: 5 days without solar charging

- Capacities:

  - MLIV-1: 1400 Ah (4 sets) @ C5

  - MLIV-2: 325 Ah (1 set) @ C5

  - MLIV-3: 1400 Ah (4 sets) @ C5

Power Panel

- 24 VDC panelboard

- Standard: 16-SAMSS-518

Environmental Conditions

- System must operate at 56°C effective ambient temperature

- Suitable for Saudi desert environment

- Weatherproof and corrosion-resistant

- Service conditions per SAES-A-112

3. Applicable Standards & Which Equipment They Apply To

Solar PV System (9COM: 6000001239)

- SAES-P-128 – Off-grid solar PV system with battery storage

- SAES-P-103 – UPS & DC systems

- SAES-P-111 – Grounding

- SAES-P-100 – Basic power system design

- SAES-P-104 – Wiring methods and materials

- SAES-A-112 – Environmental / temperature considerations

- SAES-J-902 – Electrical systems for instrumentation

- SAES-M-001 – Structural design criteria

- 12-SAMSS-007 – Supporting structures design

- AA-036322.001 – Anchor bolt details

- DD-950022 – Ground connection details

Batteries (9COM: 6000001076)

- 17-SAMSS-511 – Stationary storage batteries

- SAEP-350 – Maintenance/testing of industrial stationary batteries

Power Panels (9COM: 6000000859)

- 16-SAMSS-518 – Low-voltage panelboards

Documentation, SPDP, Packaging

- SAEP-31 – Spare parts data package requirements

- MS 8314-xx series – Packing specifications

- SAEP-302 – Waiver of mandatory requirements

- SAEP-385 – Preservation of materials

4. All Equipment Required as Part of the System

Primary Equipment

- Solar Panels (PV modules)

- Solar Array Support Structure

- Array Junction Boxes

- Combiner Junction Box

- Solar Charge Controllers (PWM type)

- Battery Breaker/Isolator Box (implied through control center but not explicitly named)

- Nickel-Cadmium Batteries (24 VDC system)

- Battery Enclosures (implied via datasheets, not explicitly named)

- 24 VDC Power Panel

- Cables & Wiring (per SAES-P-104)

- Cable glands (not explicitly stated but part of wiring hardware)

- Grounding materials & lightning protection system (per SAES-P-111)

Other System Components

- Metering and control circuits

- Interconnecting hardware

- Supporting structures

- Weatherproof enclosures

- Anchor bolts

5. All Vendor Responsibilities

The vendor must:

Design & Engineering

- Full system design, engineering, and sizing

- Provide solar array angle calculation

- Provide foundation loading & wind force data

- Ensure compliance with all ARAMCO standards

Fabrication & Supply

- Supply all equipment and hardware

- Manufacturing, assembly, shop testing, packing

- Provide all accessories, software, and documentation needed for a fully functional system

- Supply items even if not explicitly listed but required for operation

Installation, Testing & Commissioning (as required)

- Installation supervision

- Commissioning & site acceptance testing

- Training & system support

- Technical assistance during installation

Documentation

- Submit complete SPDP package

- Provide datasheets/catalogs for all equipment

- Submit SVL for ARAMCO approval (all items must be from approved sources)

- Provide all engineering docs, drawings, calculations, and reports

Compliance & Quality Requirements

- Follow ARAMCO engineering standards

- Ensure equipment withstands environmental and structural requirements

- Meet packing, inspection, and testing requirements

If you want, I can also prepare:

✔ A client-ready PDF summary
✔ A comparison table between your standard system and the BOQ
✔ A list of missing items or clarifications you need to ask ARAMCO

Just tell me.

You said:

Give me 2 & 3.

ChatGPT said:

Sure — here are the two items you requested:

2. Comparison Table (Your Standard System vs This BOQ Requirements)

This table shows how the typical solar system you supply compares with the specific ARAMCO requirements listed in this BOQ.

| System Component | Your Usual Standard (Typical Vendor Offering) | ARAMCO BOQ Requirement (This Project) | Comments |
| --- | --- | --- | --- |
| Solar Panels | Standard mono/poly PV modules | Mono or poly PV modules; each string must have Schottky blocking diode | Blocking diode is specifically mandatory |
| Solar Structure | Hot-dip galvanized steel, standard wind rating 120–140 km/h | Hot-dip galvanized per ASTM A123, must withstand 145 km/h | Need to ensure structural calcs meet wind requirement |
| Tilt & Orientation | Usually based on site latitude | Must be optimized for winter solstice and face south ±5° | BOQ gives stricter orientation criteria |
| Array Junction Box | Standard DC combiner boxes | Must include module junction boxes and combiner box per BOQ | Alignment required |
| Charge Controller | MPPT or PWM depending on design | PWM only + vendor must provide datasheet | Must ensure PWM type is acceptable for your system |
| Battery Type | VRLA Gel / AGM / Lithium normally | Strictly Nickel-Cadmium per 17-SAMSS-511 | Major difference – battery must be Ni-Cd |
| Battery Capacity | Typically designed based on load | BOQ specifies exact capacities: 1400 Ah (4 sets), 325 Ah (1 set) | Must follow BOQ capacities |
| Battery Autonomy | Usually 2–3 days | 5 days minimum autonomy | System sizing must be larger |
| Battery Enclosure | Standard battery rack/enclosure | Racks/enclosures implied but must comply with Ni-Cd requirements | Must match ARAMCO Ni-Cd specs |
| Power Panel (24 VDC) | Standard LV DC panel | Must comply with 16-SAMSS-518 | Ensure design matches ARAMCO standard |
| Grounding System | Standard grounding | Must comply with SAES-P-111 + DD-950022 | Specific grounding drawing required |
| Environmental Conditions | Typically designed for 45–55°C | Must operate continuously at 56°C | Thermal design must be reviewed |
| Documentation | Basic datasheets/drawings | Full SPDP, SVL, datasheets, structure calcs, anchor bolt data | Heavier documentation load |
| Testing | Factory testing | Must comply with 175-000003 | Follow ARAMCO testing instructions |
| Installation Support | Optional | Vendor must provide installation supervision & commissioning if required | Service scope is conditional |
| Packaging | Standard wooden crates | Must follow MS 8314-xx packing standards | ARAMCO-specific packing rules |

If you'd like, I can convert this into a client-ready submission note.

3. List of Missing Information / Clarifications to Ask ARAMCO

Here are all gaps in the BOQ where the client did not provide enough detail, and where you should request clarification before quoting.

Missing or Unspecified Information

- Electrical Load / System Wattage Not Provided
– No load values, current consumption, or power demand were included.
– Essential for confirming panel wattage and final array size.

- Solar Panel Wattage & Quantity Missing
– No panel wattage, efficiency, number of strings, or layout provided.

- Cable Sizes & Lengths Missing
– Cable sizing (DC & grounding) is not provided.

- Array Junction Box Specifications
– No details about:
• number of inputs/outputs
• fuse ratings
• surge protection requirements
• IP rating

- Charge Controller Model
– Only “PWM type” is specified; no:
• current rating
• voltage input range
• efficiency
• IP rating
• surge withstand capability

- Battery Enclosure Details
– No IP rating, material, cooling method or type of battery rack stated.

- Power Panel Internal Components
– The BOQ gives tag numbers but no:
• breaker sizes
• number of feeders
• metering details
• protection components

- Grounding & Lightning Protection Details
– Only reference to standard SAES-P-111 is given; no quantities or layout.

- Interconnection & Control Wiring
– No wiring schematics or I/O list included.

- Site Layout / Distance Between Components
– No site plan or distance between panel → JBs → panels → battery rooms.

- Civil/Foundation Requirements
– Vendor must design bearing loads and wind forces but:
• no soil data
• no foundation dimensions
• no depth or type of foundation provided

- Detailed List of Required Accessories
– Accessories like surge arrestors, cable trays, conduits, etc. are not specified.

How did you know what "typical Vendor offering" is?

ChatGPT said:

Good question — and you're right to challenge it.

Direct Answer:

I do not actually know your company’s typical standard offering, because you never described it.

In the comparison table, I used generic industry-standard assumptions for what most solar vendors usually supply unless ARAMCO specifies otherwise.

These are common defaults in the solar industry:

| Component | Typical Industry Default |
| --- | --- |
| Battery | VRLA / AGM / Lithium (not Ni-Cd) |
| Charge Controller | MPPT (not PWM) |
| Autonomy | 2–3 days (not 5 days) |
| Structure wind rating | 120–140 km/h common |
| Documentation | Basic datasheets (not SPDP packages) |

These are not based on your company — they are simply what is “normal” in the market.

If you'd like, I can customize the comparison

If you tell me what your standard/system normally includes, I will update the comparison table to match your actual company baseline.

For example:

- Battery type your company usually supplies

- Charge controller type

- Structure specs

- Panel wattage

- Autonomy you usually design for

- Whether you use combiner boxes

- How much documentation you normally provide

Just list them (even short bullet points), and I’ll update the comparison accurately.