## BOQ Data
Item / Question | Information Extracted from BOQ
Project Name | REPLACE 56" ABQAIQ YANBU PIPELINE (AY-1L) – SECTION 7 SOLAR POWER SYSTEM
Name of the Engineering Consultant | WORLEY
Name of the EPC | BIN QURAYA COMPANY LIMITED
Applicable 9COM numbers and their respective descriptions | 6000001239 - POWER SUPPLY SYSTEM: SOLAR, PHOTOVOLTAIC TYPE, OFF-GRID, INCLUDING ALL COMPONENTS & ACCESSORIES, 6000001076 - BATTERY: NICKEL-CADMIUM STA. STORAGE, 6000000859 - PANELBOARD; LOW VOLTAGE, NON-XPROOF
List of Standards applicable for each 9COM | SAES-P-128 - Off-grid Solar Photovoltaic (PV) System with Battery Storage, SAES-P-103 - UPS and DC Systems, SAES-P-111 - Grounding, SAES-A-112 - Meteorological and Seismic Design Data, 17-SAMSS-511 - Stationary Storage Batteries, 16-SAMSS-518 - Low Voltage Panel boards, 12-SAMSS-007 - Foundation Design, ASTM A123 - Hot-dipped galvanizing
Number of Systems | 3
Wattage / Load value for each system (if available) | System 1: 400 AMP 24VDC, System 2: 30 AMP 24VDC, System 3: 400 AMP 24VDC
Numbers of sites for each type of system
Required Battery Type | Nickel Cadmium
Required Battery Autonomy | 5 days full operation without solar charging
Required Battery Capacity | System 1: 1400 AH (4 sets) @ C5, System 2: 325 AH (1 set) @ C5, System 3: 1400 AH (4 sets) @ C5
Environmental Conditions | Continuous operation at 56°C effective ambient temperature, wind velocities in excess of 145 KM/hour, weatherproof and corrosive resistant
Temperature Range | Up to 56°C effective ambient temperature
Support Structure details / specifications | Hot-dipped galvanized per ASTM A123, non-corrosive materials, designed per 12-SAMSS-007, optimum azimuth and tilt angle for winter solstice, directed toward geographical south (±5 degrees)
Specifications or details of any other equipment | Mono-crystalline and poly-crystalline solar modules only, Schottky blocking diodes for each string, PWM charge controller, fused disconnect combiner, panels with 5+ years field use in Saudi Arabia or Middle Eastern desert environments
Any other service required by the client | Design and engineering, assembly and supply, installation supervision, commissioning and site acceptance testing, training and system support, spare parts data package (SPDP) for 2 years operation, start-up commissioning spare parts