## BOQ Data
Item / Question | Information Extracted from BOQ
Project Name | REPLACE 56" ABQAIQ YANBU PIPELINE (AY-1L) – SECTION 7 SOLAR POWER SYSTEM
Name of the Engineering Consultant | WORLEY
Name of the EPC | BIN QURAYA COMPANY LIMITED
Applicable 9COM numbers and their respective descriptions | 6000001239 - POWER SUPPLY SYSTEM: SOLAR, PHOTOVOLTAIC TYPE, OFF-GRID, INCLUDING ALL COMPONENTS & ACCESSORIES, 6000001076 - BATTERY: NICKEL-CADMIUM STA. STORAGE, 6000000859 - PANELBOARD; LOW VOLTAGE, NON-XPROOF
List of Standards applicable for each 9COM | 17-SAMSS-511 - Stationary Storage Batteries, 16-SAMSS-518 - Low Voltage Panel boards, 12-SAMSS-007 - Foundation Design, SAES-P-128 - Off-grid Solar Photovoltaic (PV) System with Battery Storage, SAES-P-103 - UPS and DC Systems, SAES-P-111 - Grounding, SAES-A-112 - Meteorological and Seismic Design Data, ASTM A123 - Hot-dipped galvanized coating
Number of Systems | 3 systems
Wattage / Load value for each system (if available) | System 1: 400 AMP/24VDC, System 2: 30 AMP/24VDC, System 3: 400 AMP/24VDC
Numbers of sites for each type of system
Required Battery Type | Nickel Cadmium (NiCd)
Required Battery Autonomy | 5 days full operation without solar charging
Required Battery Capacity | System 1: 1400 AH @ C5 (4 sets), System 2: 325 AH @ C5 (1 set), System 3: 1400 AH @ C5 (4 sets)
Environmental Conditions | Continuous operation at 56°C effective ambient temperature, wind velocities up to 145 KM/hour, Middle Eastern desert environments
Temperature Range | Up to 56°C effective ambient temperature
Support Structure details / specifications | Hot-dipped galvanized per ASTM A123, non-corrosive materials, designed per 12-SAMSS-007, withstand wind velocities over 145 KM/hour, optimum azimuth and tilt angle for winter solstice, directed toward geographical south (±5 degrees)
Specifications or details of any other equipment | 24VDC system, mono-crystalline and poly-crystalline modules only, PMW charge controller, Schottky blocking diode per string, fused disconnect combiner, weatherproof and corrosive resistant, 5 years field use demonstration in Saudi Arabia or Middle Eastern desert environments required
Any other service required by the client | Design and engineering, supply of materials, manufacturing, assembly, shop testing, packing, installation supervision, commissioning/site acceptance testing, training and system support, technical assistance, spare parts data package (SPDP) for 2 years operation, start-up commissioning spare parts