## Sheet1
Solar Panels Configuration? 1x100% or 2x50%?
Array Junction Boxes required?
Charge Controller Type? MPPT or PWM?
List of Hard-wired signals to be transmitted from the charge controllers?
Any other signals/alarms to be transmitted from charge controllers
Battery Breaker Box required?
# of Battery breaker boxes required?
Battery configuration? 1x100% or 2x50%?
Battery type? NiCd or VRLA?
How many cells in series?
How many strings of batteries?
Required Battery Enclosure IP rating?
Required Back-up?
Panel Board / DB / Load Output Station required?
Enclosure rating of the LOS?
List the Number of breakers and their ratings given in the LOS
List down the relevant notes for each equipment in front of each equipment.
Also highlight any other equipment which got missed in this format.
Any other point which is critical to design the system?
Responses from ChatGPT
Item / Question | MLIV-1 @ KM 3.40 (SP-001) | MLIV-2 @ KM 19.40 (SP-002) | MLIV-3 @ KM 34.00 (SP-003)
Solar panels configuration? 1×100% or 2×50%? | Not stated – single array K18-(SP-001)-PV-0001 shown; no redundancy split mentioned. | Not stated – single array K18-(SP-002)-PV-0001 shown. | Not stated – single array K18-(SP-003)-PV-0001 shown.
Array Junction Boxes required? | Yes – PV junction box / “PHOTOVOLTAIC ARRAY JUNCTION BOX, NEMA-4/4X” shown between array and controller. | Yes – PV junction box symbol in NEMA-4 shown. | Yes – PV junction box symbol in NEMA-4 shown.
Charge controller type? MPPT or PWM? | MPPT – notes call for fused disconnect combiner between PV arrays and MPPT charge controller. | MPPT (same note set). | MPPT (same note set).
List of hard-wired signals from charge controller to RTU | 1- Battery bank A/B voltage low alarm 2- Charger fault & common alarm 3- Battery MCCB open 4- Low battery state of charge 5- Load disconnected | Same signal list as MLIV-1. | Same signal list as MLIV-1.
Any other signals/alarms from charge controller | Local LCD display (alarms) at controller. | Same – local LCD alarms. | Same – local LCD alarms.
Battery breaker box required? | Yes – “BREAKER IN NEMA-4X ENCLOSED CIRCUIT” between battery bank and DC bus. | Yes – same arrangement. | Yes – same arrangement.
No. of battery breaker boxes required? | 1 enclosure indicated for the battery MCCB. | 1 enclosure indicated. | 1 enclosure indicated.
Battery configuration? 1×100% or 2×50%? | Two banks A & B indicated; likely 2×50%, but % not explicitly written → not explicitly stated. | Banks A & B indicated; split not explicitly stated. | Banks A & B indicated; split not explicitly stated.
Battery type? NiCd or VRLA? | Ni-Cd stationary batteries. | Ni-Cd. | Ni-Cd.
How many cells in series? | 19 cells in series. | 19 cells in series. | 19 cells in series.
How many strings / sets of batteries? | 1400 Ah (4 sets) @ C5. | 325 Ah (1 set) @ C5. | 1400 Ah (4 sets) @ C5.
Required battery enclosure IP / NEMA rating? | NEMA-4 stationary battery enclosure (non-metallic FRP per notes). | NEMA-4 stationary battery enclosure. | NEMA-4 stationary battery enclosure.
Required back-up / autonomy? | 120 hours (5 days) @ C5. | 120 hours (5 days) @ C5. | 120 hours (5 days) @ C5.
Panel board / DB / LOS required? | Yes – 24 VDC power panel K18-(SP-001)-PP-0001 (LOS) + lighting control panel K18-(SP-001)-CP-0001. | Yes – 24 VDC power panel K18-(SP-002)-PP-0001. | Yes – 24 VDC power panel K18-(SP-003)-PP-0001 + lighting control panel K18-(SP-003)-CP-0001.
Enclosure rating of LOS / power panel | NEMA-4X, outdoor. | NEMA-4X, outdoor. | NEMA-4X, outdoor.
Number of breakers and ratings in LOS | Main bus: 100 A, 24 VDC, 10 kAIC, 1 s. Multiple 2-pole MCCBs mainly 30 A / 100 AF, plus some 20 A / 100 AF feeding RTU, comms and lighting; exact count to be confirmed from drawing. | Main bus: 100 A, 24 VDC, 10 kAIC, 1 s. Outgoing 2-pole breakers mostly 30 A / 100 AF with some 20 A / 100 AF for skid/loads; exact count to be confirmed. | Main bus: 100 A, 24 VDC, 10 kAIC, 1 s. Outgoing 2-pole breakers mostly 30 A / 100 AF and some 20 A / 100 AF; exact count to be confirmed.
Relevant notes for PV / charge controller | PV system & installation per SAES-P-103 & SAES-P-128; fused disconnect combiner before MPPT controller; PV equipment not in classified area; DC bus per applicable SAMSS; LV panelboard per 16-SAMSS-518; vendor to confirm number of PV panels, array arrangement and controller ratings; ambient derating per SAES-A-112; Saudi Aramco standards cut-off May 2023. | Same note set as MLIV-1. | Same note set as MLIV-1.
Relevant notes for batteries / enclosure | Ni-Cd per 17-SAMSS-511 & NFPA-70; outdoor battery enclosure non-metallic (fiberglass-reinforced) per SAES-P-128; alarms/instrumentation per SAES-P-103 & 17-SAMSS-511; vendor to confirm Ah capacity; ambient temperature consideration for MCCBs. | Same as MLIV-1, with 325 Ah capacity. | Same as MLIV-1, with 1400 Ah (4 sets).
Other equipment not explicitly covered above | RTU K18-RTU-740; lighting contactor panel; photo cell; outdoor light; communication equipment feeders; lighting shelter; spare feeders; cables tagged K18-PC-3921…3926 etc. | HOV loads (K18-HOV-00773/74/75/00823/00824); DIT device K18-DIT-00912; surge-relief skid K18-U-0004; spare feeders; cables K18-PC-3941…3947. | RTU K18-RTU-750; lighting contactor & photo cell; DC power panel in shelter; HOV loads K18-HOV-00776/77/78; spare feeders; cables K18-PC-3961…3969.
Any other critical points for system design | 5-day autonomy; keep PV/controls out of classified areas; all alarms/status to RTU (Ethernet + hardwired); ambient derating for breakers; comply with listed SAES/SAMSS; Saudi Aramco standards cut-off May 2023. | Same design constraints as MLIV-1, with smaller battery (325 Ah). | Same as MLIV-1, with larger 1400 Ah battery and additional loads (more HOVs & lighting).