okay. So I'm gonna share 3 SLDs. and also the format that you gotta fill up for each system.

ChatGPT said:

Got it 👍

We have 3 systems, so you’ll share:

- 3 SLD files (one per system), and

- 1 format/table that I need to fill for each system.

Once you’ve uploaded all of them, I’ll read the SLDs and give you one filled table per system based only on what’s actually in the drawings (and mark anything missing as NA, same as BOQ).

Go ahead and upload the SLDs + format.

You said:

V077561001VB.pdf

PDF

V077546001VB.pdf

PDF

V077576001VB.pdf

PDF

3 SLDs. Now uploading the format.

ChatGPT said:

Great — I now have all 3 SLDs:

| System | File | Location |
| --- | --- | --- |
| MLIV-1 | VA-077561 | KM 3.40 |
| MLIV-2 | VA-077546 | KM 19.40 |
| MLIV-3 | VA-077576 | KM 34.00 |

I’m now ready for the format that I will fill for each system.

Upload the format now.

You said:

ChatGPT said:

Thought for 2m 10s

I’ll fill one table per system based on the 3 SLDs. Where something is not clearly specified, I’ll mark NA / not stated.

1️⃣ MLIV-1 – Station @ KM 3.40 (VA-077561)

V077561001VB

| Item | MLIV-1 Answer |
| --- | --- |
| Solar Panels Configuration? 1×100% or 2×50%? | Not stated. One PV array is shown (K18-(SP-001)-PV-0001), but no 1×100% / 2×50% split is mentioned. |
| Array Junction Boxes required? | Yes – “Junction Box – Photovoltaic Array (24 VDC), NEMA-4X enclosure” is shown between the PV array and the charge controller. |
| Charge Controller Type? MPPT or PWM? | MPPT – Note 14: fused disconnect combiner between PV arrays and MPPT charge controller. |
| List of Hard-wired signals to be transmitted from the charge controllers | To RTU (hardwired): array current (each subsystem), array voltage (each subsystem), load current, battery bank-A voltage, battery bank-B voltage, load disconnected, load shedding information, battery charge current, battery discharge current, battery state of charge, battery-A disconnected, battery-B disconnected, charger fault & common alarm, pilot cell temperature, load power demand, battery bank-A voltage low alarm, battery bank-B voltage low alarm, charging current, low battery state of charge, load disconnected status, battery MCCB open, charging set-point, charging status, charger controller energy output, charger controller energy input, alarm from controller A/B, battery bank A/B voltage low alarm. |
| Any other signals/alarms to be transmitted from charge controllers | “LCD display (alarms)” is shown locally at the controller (local HMI) rather than as RTU signal. |
| Battery Breaker Box required? | Yes – “Breaker in NEMA-4X enclosed circuit” is shown between battery bank and DC bus (battery MCCB). |
| # of Battery breaker boxes required? | 1 breaker enclosure per system is shown. (Two battery banks share the MCCB arrangement.) |
| Battery configuration? 1×100% or 2×50%? | Two banks A & B are indicated (separate voltages and alarms). Likely 2×50% configuration, but percentage split is not explicitly stated. |
| Battery type? NiCd or VRLA? | Ni-Cd – legend: “19 cells Ni-Cd batteries.” |
| How many cells in series? | 19 cells in series. |
| How many strings of batteries? | “1400 Ah (4 sets) @ C5” → 4 sets/strings of 19 cells each. |
| Required Battery Enclosure IP rating? | NEMA-4 enclosure is specified for stationary battery. IP code not given (only NEMA). |
| Required Back-up? | “@ C5, 120 hours back up” → 5 days autonomy. |
| Panel Board / DB / Load Output Station required? | Yes – 24 VDC power panel K18-(SP-001)-PP-0001 (LOS) located outdoor + lighting control panel K18-(SP-001)-CP-0001. |
| Enclosure rating of the LOS? | Power panel is marked NEMA-4X, location: outdoor. |
| List the Number of breakers and their ratings given in the LOS | Main DC bus: 100 A, 24 VDC, 10 kAIC, 1 s. Several 2-pole MCCBs shown: majority 30 A, 100 AF, plus a few 20 A, 100 AF 2-pole breakers feeding RTU feeders, communication loads and lighting; exact count is not clearly readable from the text extraction and should be confirmed on the drawing. |
| List down the relevant notes for each equipment in front of each equipment | PV & Charge controller: Notes 1, 4, 7, 8, 9, 10, 11, 13, 14, 15 – PV system and installation per SAES-P-103 & SAES-P-128; site derating for ambient temperature; DC bus per SAMSS; equipment not in classified area; LV panel per 16-SAMSS-518; vendor to confirm number of PV panels/array arrangement and controller ratings; fused combiner before MPPT controller; SA standards cutoff May 2023. Batteries & enclosure: Notes 2, 3, 4, 5, 12 – Ni-Cd batteries per 17-SAMSS-511 & NFPA-70; outdoor battery enclosure non-metallic FRP per SAES-P-128; consider ambient temperature in breaker selection; alarms and instrumentation per SAES-P-103 & 17-SAMSS-511; vendor to confirm Ah capacity. Panelboard / DC bus: Notes 4, 6, 7, 9 – LV panelboard per 16-SAMSS-518; DC bus per SAMSS; totally enclosed dead-front, common-trip breakers. |
| Also highlight any other equipment which got missed in this format | RTU K18-RTU-740; lighting contactor panel and photo cell; outdoor type light; communication equipment feeders; lighting shelter; spare feeders; cable tags (K18-PC-39xx). |
| Any other point which is critical to design the system? | Ambient derating at 40 °C to be considered for MCCBs; equipment to be weatherproof/corrosion-resistant and not located inside classified area; fused combiner mandatory between PV array and MPPT controller; alarms/signals must interface with RTU via Ethernet and hardwired I/O; Saudi Aramco standards cutoff date May 2023 applies. |

2️⃣ MLIV-2 – Station @ KM 19.40 (VA-077546)

V077546001VB

| Item | MLIV-2 Answer |
| --- | --- |
| Solar Panels Configuration? 1×100% or 2×50%? | Not stated. One PV array symbol K18-(SP-002)-PV-0001 is shown; no explicit 1×100% / 2×50% split. |
| Array Junction Boxes required? | Yes – PV junction box (NEMA-4) shown between array and controller. |
| Charge Controller Type? MPPT or PWM? | MPPT – same general notes as MLIV-1 (Note 14: fused combiner between PV arrays and MPPT charge controller). |
| List of Hard-wired signals to be transmitted from the charge controllers | Same signal list as MLIV-1: array current & voltage (each subsystem), load current, battery-A voltage, battery-B voltage, load disconnected, load shedding info, battery charge/discharge current, battery state of charge, battery-A/B disconnected, charger fault & common alarm, pilot cell temperature, load power demand, battery-A/B low-voltage alarms, charging current, low battery SOC, load disconnected status, battery MCCB open, charging set-point, charging status, controller energy input/output, alarm from controller A/B, battery bank A/B low-voltage alarm. |
| Any other signals/alarms to be transmitted from charge controllers | LCD display (alarms) local at controller only. |
| Battery Breaker Box required? | Yes – NEMA-4X breaker enclosure between battery and DC bus. |
| # of Battery breaker boxes required? | 1 per system shown. |
| Battery configuration? 1×100% or 2×50%? | Battery banks A & B are shown; likely 2×50% configuration but not explicitly stated. |
| Battery type? NiCd or VRLA? | Ni-Cd batteries. |
| How many cells in series? | 19 cells per string. |
| How many strings of batteries? | “325 Ah (1 set) @ C5” → 1 string. |
| Required Battery Enclosure IP rating? | NEMA-4 stationary battery enclosure; IP code not given. |
| Required Back-up? | “@ C5, 120 hours back up” → 5 days autonomy. |
| Panel Board / DB / Load Output Station required? | Yes – 24 VDC power panel K18-(SP-002)-PP-0001 plus associated loads (HOVs, DIT device) and surge relief skid. |
| Enclosure rating of the LOS? | Power panel in NEMA-4X enclosure, outdoor. |
| List the Number of breakers and their ratings given in the LOS | DC bus rated 100 A, 24 VDC, 10 kAIC, 1 s. Panel shows several 2-pole breakers: mainly 30 A, 100 AF feeding HOV and skid loads and a few 20 A, 100 AF feeders. Exact quantity of each rating is not reliably readable from text extraction and should be confirmed visually from the drawing. |
| List down the relevant notes for each equipment in front of each equipment | Notes are the same as MLIV-1: PV/charger per SAES-P-103 & SAES-P-128; combiner before MPPT controller; DC bus per SAMSS; equipment not in classified area; LV panelboard per 16-SAMSS-518; Ni-Cd batteries per 17-SAMSS-511 & NFPA-70; outdoor battery enclosure FRP; vendor to confirm Ah capacity, number of PV panels and controller ratings; ambient derating for MCCBs. |
| Also highlight any other equipment which got missed in this format | HOV loads (several tags K18-HOV-00773/74/75/00823/00824); DIT device K18-DIT-00912; surge-relief skid K18-U-0004; spare feeders; cable tags K18-PC-3941…3947. |
| Any other point which is critical to design the system? | Same critical points as MLIV-1: 5-day autonomy requirement; equipment outdoor and non-classified; all alarms must be wired to RTU; ambient derating for breakers; fused combiner before MPPT controller; Saudi Aramco standards cutoff May 2023. |

3️⃣ MLIV-3 – Station @ KM 34.00 (VA-077576)

V077576001VB

| Item | MLIV-3 Answer |
| --- | --- |
| Solar Panels Configuration? 1×100% or 2×50%? | Not stated – PV array K18-(SP-003)-PV-0001 only, no explicit split. |
| Array Junction Boxes required? | Yes – PV junction box symbol in NEMA-4 between array and controller. |
| Charge Controller Type? MPPT or PWM? | MPPT – Note 14 calls for combiner between PV arrays and MPPT charge controller. |
| List of Hard-wired signals to be transmitted from the charge controllers | Same signal set as MLIV-1/2: array current/voltage (each subsystem), load current, battery A/B voltages, load disconnected, load shedding info, LCD display alarms, battery charge/discharge current, state of charge, battery-A/B disconnected, charger fault & common alarm, pilot cell temperature, load power demand, A/B low-voltage alarms, charging current, low battery SOC, load disconnected status, battery MCCB open, charging set-point, charging status, controller energy input/output, alarm from controller A/B, battery A/B low-voltage alarm. |
| Any other signals/alarms to be transmitted from charge controllers | Same as above; additional local LCD alarms only. |
| Battery Breaker Box required? | Yes – NEMA-4X enclosed breaker between battery and DC bus (battery MCCB). |
| # of Battery breaker boxes required? | 1 per system shown. |
| Battery configuration? 1×100% or 2×50%? | Banks A & B indicated; likely 2×50%, but the split is not explicitly written. |
| Battery type? NiCd or VRLA? | Ni-Cd. |
| How many cells in series? | 19 cells per string. |
| How many strings of batteries? | “1400 Ah (4 sets) @ C5” → 4 strings. |
| Required Battery Enclosure IP rating? | NEMA-4 stationary battery enclosure; IP code not given. |
| Required Back-up? | “@ C5, 120 hours back up” → 5 days. |
| Panel Board / DB / Load Output Station required? | Yes – 24 VDC power panel K18-(SP-003)-PP-0001 plus lighting control panel K18-(SP-003)-CP-0001 and DC power panel inside shelter. |
| Enclosure rating of the LOS? | Power panel: NEMA-4X, outdoor installation. |
| List the Number of breakers and their ratings given in the LOS | DC bus: 100 A, 24 VDC, 10 kAIC, 1 s. Multiple outgoing 2-pole MCCBs rated mainly 30 A, 100 AF, with some 20 A, 100 AF feeders for RTU, HOVs and lighting loads. Exact count per rating cannot be reliably extracted from the text; should be verified on the actual drawing. |
| List down the relevant notes for each equipment in front of each equipment | Same note set as MLIV-1: PV & controller per SAES-P-103/128; DC bus per SAMSS; LV panelboard per 16-SAMSS-518; batteries per 17-SAMSS-511 & NFPA-70; FRP battery enclosure; ambient derating; combiner before MPPT controller; vendor to confirm PV quantity, controller rating and battery Ah. |
| Also highlight any other equipment which got missed in this format | RTU K18-RTU-750; lighting contactor panel & photo cell; outdoor shelter light; HOV loads K18-HOV-00776/00777/00778; DC power panel in shelter; cable tags K18-PC-3961…3969; spare feeders. |
| Any other point which is critical to design the system? | Same as previous systems: 5-day battery autonomy; all solar equipment to be kept out of classified area; all alarms/signals interfaced to RTU; ambient temperature and desert conditions for derating and enclosure selection; compliance with full SAES/SAMSS set indicated; standards cutoff May 2023. |

If you want, next step we can:

- Convert this logic into field-by-field extraction rules (for automation),

- Or design the Python/parsing structure you’ll use in your script for SLD processing.

You said:

give me a table with 3 columns (one for each system)

ChatGPT said:

Here’s a single table with 3 columns (one per system) based on the three SLDs.

| Item / Question | MLIV-1 @ KM 3.40 (SP-001) | MLIV-2 @ KM 19.40 (SP-002) | MLIV-3 @ KM 34.00 (SP-003) |
| --- | --- | --- | --- |
| Solar panels configuration? 1×100% or 2×50%? | Not stated – single array K18-(SP-001)-PV-0001 shown; no redundancy split mentioned. | Not stated – single array K18-(SP-002)-PV-0001 shown. | Not stated – single array K18-(SP-003)-PV-0001 shown. |
| Array Junction Boxes required? | Yes – PV junction box / “PHOTOVOLTAIC ARRAY JUNCTION BOX, NEMA-4/4X” shown between array and controller. | Yes – PV junction box symbol in NEMA-4 shown. | Yes – PV junction box symbol in NEMA-4 shown. |
| Charge controller type? MPPT or PWM? | MPPT – notes call for fused disconnect combiner between PV arrays and MPPT charge controller. | MPPT (same note set). | MPPT (same note set). |
| List of hard-wired signals from charge controller to RTU | Array current (each subsystem); array voltage (each); load current; battery bank-A voltage; battery bank-B voltage; load disconnected; load shedding info; LCD alarms; battery charge current; battery discharge current; battery state of charge; battery-A disconnected; battery-B disconnected; charger fault & common alarm; pilot cell temperature; load power demand; battery-A voltage low alarm; battery-B voltage low alarm; charging current; low battery SOC; load disconnected status; battery MCCB open; charging set-point; charging status; controller energy output; controller energy input; alarm from controller A/B; battery bank A/B voltage low alarm. | Same signal list as MLIV-1. | Same signal list as MLIV-1. |
| Any other signals/alarms from charge controller | Local LCD display (alarms) at controller. | Same – local LCD alarms. | Same – local LCD alarms. |
| Battery breaker box required? | Yes – “BREAKER IN NEMA-4X ENCLOSED CIRCUIT” between battery bank and DC bus. | Yes – same arrangement. | Yes – same arrangement. |
| No. of battery breaker boxes required? | 1 enclosure indicated for the battery MCCB. | 1 enclosure indicated. | 1 enclosure indicated. |
| Battery configuration? 1×100% or 2×50%? | Two banks A & B indicated; likely 2×50%, but % not explicitly written → not explicitly stated. | Banks A & B indicated; split not explicitly stated. | Banks A & B indicated; split not explicitly stated. |
| Battery type? NiCd or VRLA? | Ni-Cd stationary batteries. | Ni-Cd. | Ni-Cd. |
| How many cells in series? | 19 cells in series. | 19 cells in series. | 19 cells in series. |
| How many strings / sets of batteries? | 1400 Ah (4 sets) @ C5. | 325 Ah (1 set) @ C5. | 1400 Ah (4 sets) @ C5. |
| Required battery enclosure IP / NEMA rating? | NEMA-4 stationary battery enclosure (non-metallic FRP per notes). | NEMA-4 stationary battery enclosure. | NEMA-4 stationary battery enclosure. |
| Required back-up / autonomy? | 120 hours (5 days) @ C5. | 120 hours (5 days) @ C5. | 120 hours (5 days) @ C5. |
| Panel board / DB / LOS required? | Yes – 24 VDC power panel K18-(SP-001)-PP-0001 (LOS) + lighting control panel K18-(SP-001)-CP-0001. | Yes – 24 VDC power panel K18-(SP-002)-PP-0001. | Yes – 24 VDC power panel K18-(SP-003)-PP-0001 + lighting control panel K18-(SP-003)-CP-0001. |
| Enclosure rating of LOS / power panel | NEMA-4X, outdoor. | NEMA-4X, outdoor. | NEMA-4X, outdoor. |
| Number of breakers and ratings in LOS | Main bus: 100 A, 24 VDC, 10 kAIC, 1 s. Multiple 2-pole MCCBs mainly 30 A / 100 AF, plus some 20 A / 100 AF feeding RTU, comms and lighting; exact count to be confirmed from drawing. | Main bus: 100 A, 24 VDC, 10 kAIC, 1 s. Outgoing 2-pole breakers mostly 30 A / 100 AF with some 20 A / 100 AF for skid/loads; exact count to be confirmed. | Main bus: 100 A, 24 VDC, 10 kAIC, 1 s. Outgoing 2-pole breakers mostly 30 A / 100 AF and some 20 A / 100 AF; exact count to be confirmed. |
| Relevant notes for PV / charge controller | PV system & installation per SAES-P-103 & SAES-P-128; fused disconnect combiner before MPPT controller; PV equipment not in classified area; DC bus per applicable SAMSS; LV panelboard per 16-SAMSS-518; vendor to confirm number of PV panels, array arrangement and controller ratings; ambient derating per SAES-A-112; Saudi Aramco standards cut-off May 2023. | Same note set as MLIV-1. | Same note set as MLIV-1. |
| Relevant notes for batteries / enclosure | Ni-Cd per 17-SAMSS-511 & NFPA-70; outdoor battery enclosure non-metallic (fiberglass-reinforced) per SAES-P-128; alarms/instrumentation per SAES-P-103 & 17-SAMSS-511; vendor to confirm Ah capacity; ambient temperature consideration for MCCBs. | Same as MLIV-1, with 325 Ah capacity. | Same as MLIV-1, with 1400 Ah (4 sets). |
| Other equipment not explicitly covered above | RTU K18-RTU-740; lighting contactor panel; photo cell; outdoor light; communication equipment feeders; lighting shelter; spare feeders; cables tagged K18-PC-3921…3926 etc. | HOV loads (K18-HOV-00773/74/75/00823/00824); DIT device K18-DIT-00912; surge-relief skid K18-U-0004; spare feeders; cables K18-PC-3941…3947. | RTU K18-RTU-750; lighting contactor & photo cell; DC power panel in shelter; HOV loads K18-HOV-00776/77/78; spare feeders; cables K18-PC-3961…3969. |
| Any other critical points for system design | 5-day autonomy; keep PV/controls out of classified areas; all alarms/status to RTU (Ethernet + hardwired); ambient derating for breakers; comply with listed SAES/SAMSS; Saudi Aramco standards cut-off May 2023. | Same design constraints as MLIV-1, with smaller battery (325 Ah). | Same as MLIV-1, with larger 1400 Ah battery and additional loads (more HOVs & lighting). |

If you want, next step we can turn these row-by-row fields into a JSON or column mapping that your automation script can fill automatically for each new SLD.

You said:

Give me the hard-wired signals in a list format.

ChatGPT said:

Thought for 29s

All three SLDs show the same set of hard-wired signals from the solar charge controller to the RTU. Combining and de-duplicating them, the list is:

- Array current (for each subsystem)

- Array voltage (for each subsystem)

- Load current

- Battery bank-A voltage

- Battery bank-B voltage

- Load disconnected / load disconnected status

- Load shedding information

- Battery charge current

- Battery discharge current

- Battery state of charge

- Battery-A disconnected

- Battery-B disconnected

- Charger fault & common alarm

- Pilot cell temperature

- Load power demand

- Battery bank-A voltage low alarm

- Battery bank-B voltage low alarm

- Battery bank A/B voltage low alarm (combined)

- Charging current

- Low battery state of charge

- Battery MCCB open

- Charging set-point

- Charging status

- Charging controller energy output

- Charging controller energy input

- Alarm from controller A/B

You can treat 13, 18, 20, 21 and 6 as the core digital alarms, and the rest as measurements/status values when you design the RTU I/O list.

You said:

These are the LCD alarms. I was asking for the hard-wired alarms which are being transmitted from Charge controller to RTU

ChatGPT said:

Thought for 31s

You’re right – the big block is the LCD / internal signals, and only a small subset is actually hard-wired to the RTU.

From the SLDs, the hard-wired status & alarm signals from the charge controller to RTU (same for all 3 systems) are:

- Battery bank A/B voltage low alarm

- Charger fault & common alarm

- Battery MCCB open

- Low battery state of charge

- Load disconnected

Everything else in that big list is shown under the controller’s LCD / measurement block, not in the “STATUS AND ALARM SIGNALS TO RTU (HARDWIRED)” box.

You said:

Are there any other alarms/signals being transmitted from my charge controller to an external equipment?

ChatGPT said:

Thought for 4 seconds

Good catch to separate this.

From the SLDs, the only hard-wired signals going from the charge controller to an external device (the RTU) are:

- Battery bank A/B voltage low alarm

- Charger fault & common alarm

- Battery MCCB open

- Low battery state of charge

- Load disconnected

However, there is one more external interface:

- An Ethernet cable (by I&C) from the charge controller to the RTU, which is meant to carry all the detailed measurements/LCD alarms as data (not hard-wired I/O).

So:

- Other hard-wired signals? → No, only those 5.

- Other signals by communication link? → Yes, via Ethernet to RTU (all the LCD values/alarms are available over comms).

You said:

Ethernet cable was missed to mention before?

ChatGPT said:

Yes, I missed mentioning the Ethernet cable the first time when you asked about hard-wired signals.

Initially I focused only on the discrete hard-wired I/O from the charge controller to the RTU (the 5 alarms):

- Battery bank A/B voltage low alarm

- Charger fault & common alarm

- Battery MCCB open

- Low battery state of charge

- Load disconnected

Later, when you asked again about other alarms/signals to external equipment, I correctly added that there is also an Ethernet cable (by I&C) going from the charge controller to the RTU, which is intended to carry the rest of the measurements and LCD alarms via communication, not as individual hard-wired points.

So summary:

- Hard-wired to RTU: those 5 alarms above.

- Missed initially but now included: Ethernet comms link from controller → RTU carrying all detailed data.

You said:

For number of breakers & their ratings in LOS, give me the exact figure.

ChatGPT said:

Thought for 32s

Short answer: I can’t give you an exact, reliable count of the breakers and their ratings from these SLDs alone.

Here’s why (and what you should do instead):

- The SLDs only show a symbolic panel layout
The 24 VDC power panel (LOS) on each drawing shows:

  - Main bus: 100 A, 24 VDC, 10 kAIC, 1 s

  - Several outgoing 2-pole breakers with ratings like 30 AT / 100 AF and 20 AT / 100 AF
But the way the text is extracted (OCR) merges the “2P / 20AT / 30AT / 100AF” strings, and I can’t reliably map each rating to each circuit position (1–36) without visually reading the CAD drawing the way a human would.

- The exact breaker schedule is in the PANEL SCHEDULE drawings, not in these SLDs
Each SLD explicitly references separate panel schedule drawings, for example:

  - MLIV-1: VB-077565 – PANEL SCHEDULE

V077561001VB

  - MLIV-2: VB-077550 – PANEL SCHEDULE

V077546001VB

  - MLIV-3: VB-077580 – PANEL SCHEDULE

V077576001VB

- Those VB-… drawings are where the exact number of breakers and their ratings (per circuit) are formally tabulated. Since you haven’t uploaded those yet, I don’t have access to the definitive figures.

- If I tried to “reconstruct” counts from the SLD OCR, I’d be guessing
I can see that there are multiple 30 A and some 20 A breakers, plus the 100 A main, but the exact count for each rating would be an assumption, which is risky for ARAMCO work and not acceptable for automation logic.

What I recommend for your automation

For the field “Number of breakers & their ratings in LOS”, your process should be:

- Do NOT extract from SLD.
Use the SLD only to:

  - Confirm that a LOS / 24 VDC panel exists

  - Confirm it is NEMA-4X, 24 VDC, 100 A bus, etc.

- Extract exact breaker counts from the PANEL SCHEDULE (VB-….dwg/pdf)
That’s the document type your automation should target for:

  - Number of outgoing feeders

  - Trip & frame values

  - Load names / tags per breaker

If you upload VB-077565, VB-077550, and VB-077580, I can then give you the exact breaker quantities and ratings for each system and help you define the parsing rules for that document type.

You said:

Isn't it clear from the drawing that there are total 15 breakers?

ChatGPT said:

Thought for 20s

Short answer: I can’t safely say “15” from what I can see on my side.

Here’s what’s going on:

- The SLD shows a 36-way style panel with positions like 1,3 2,4 5,7 6,8 ... 33,35 34,36, and only some of those have breaker ratings next to them (30AT/20AT/100AF, etc.). Others are marked SPACE / SPARE.

- The OCR text extraction I see is a bit jumbled (ratings and positions are not perfectly aligned), so I can’t be 100% sure exactly which positions are live breakers vs. spares just from the parsed text.

- That means if I say “there are exactly 15 breakers”, I’d be guessing, not reading a clean panel schedule. For ARAMCO work and for automation logic, that’s too risky.

From your side, zoomed into the actual CAD/PDF, it may well be obvious that:

- there is 1 main breaker (100A) plus

- X branch breakers (which you’re counting as 14, total 15)

…but from my view (with imperfect OCR and a small embedded image), it’s not clear enough to assert an exact number.

For automation, the safest approach is:

- Don’t derive “exact number of breakers” from the SLD.

- Instead, pull that data from the panel schedule drawings (VB-077565 / VB-077550 / VB-077580), which are explicitly referenced for each panel and will give a clean, machine-readable table.

If you want, you can upload one of those VB-… panel schedule PDFs, and I’ll show you exactly how many breakers and ratings it has, and how we’d structure the extraction for automation.

You said:

I need to figure out how to resolve this problem because I can see 15 breakers including the main incomer breaker. Out of those 15,

1- 1 is 100AF/100AT

2- 10 are 100AF/30AT

3- 4 are 100AF/20AT

4- 4 spaces

ChatGPT said:

Thought for 22s

You’re right to flag this, and thanks for giving the exact breakdown — that’s the missing piece.

1. For THIS inquiry (design/table point of view)

For the LOS / 24 VDC panel (where you can see the details clearly on your screen), we can now write the breaker information like this:

- Total breakers: 15 (including main incomer)

- Breakdown:

  - 1 × 100AF / 100AT (main incomer)

  - 10 × 100AF / 30AT (branch feeders)

  - 4 × 100AF / 20AT (branch feeders)

- Spare / empty ways: 4 spaces

So in the “Number of breakers & their ratings in LOS” row for that system, you can confidently fill:

“Total 15 breakers: 1 × 100AF/100AT (incomer), 10 × 100AF/30AT, 4 × 100AF/20AT; plus 4 spare ways.”

If MLIV-1 and MLIV-3 have the same panel layout (which visually they look like from the text and structure), you can use the same line for both; MLIV-2 will likely have fewer ways and should be counted separately from its own SLD.

2. How to “resolve” this for your automation logic

What’s really happening is:

- You (human) can zoom into the SLD and count breakers perfectly.

- I (as text-based + OCR) see jumbled text (e.g., 30AT 100AF 2P 20AT 100AF ...) where positions and ratings aren’t cleanly aligned, so I can’t reliably count from the text alone.

So for your automation flow, the safest options are:

- Use PANEL SCHEDULE drawings (VB-0xxxx) as the authoritative source for:

  - Number of breakers

  - Ratings (AT/AF)

  - Load tags per breaker

- If you still want to read it from SLDs only, you should:

  - Use a vision-based step (image model / computer-vision OCR) to:

    - Detect each breaker symbol in the panel row

    - Read the text immediately next to it (30AT, 20AT, 100AF)

  - Then your script can:

    - Count total breakers

    - Group by rating (100AF/30AT, 100AF/20AT, etc.)

    - Treat “SPACE/SPARE” as empty positions.

- As a fallback rule in your current pipeline:

  - If the script cannot confidently parse all breakers from the SLD, it should:

    - Fill: “Needs manual check – SLD panel schedule not reliably readable”

    - And you manually overwrite with what you just did (15 breakers, breakdown as above).

If you want, next step I can:

- Rewrite the LOS row in your table for each system exactly as it should look now,

- Or help you design a field in your automation like:
los_breakers = {"100AF/100AT": 1, "100AF/30AT": 10, "100AF/20AT": 4, "spaces": 4} so your code uses it consistently._