1. Extract the following fields for each system and present the results in a table (one column per system). If any area or text is unreadable, try to zoom-in and read. Every corner of the document should be zoomed-in and read.

A. Solar Panels / PV

- Solar configuration: 1×100% or 2×50%

- PV Array Junction Box required?

- Charge controller type: MPPT or PWM

B. Charge Controller → RTU

- Hard-wired signals only (do NOT include LCD/internal alarms)

- List exactly the hard-wired alarms shown on SLD (typically: Battery A/B low voltage, Charger fault/common alarm, Battery MCCB open, Low battery SOC, Load disconnected).

- State if an Ethernet cable is shown between controller → RTU.

C. Battery System

- Battery breaker box required?

- Number of battery breaker boxes

- Battery configuration (1×100% or 2×50%)

- Battery type (NiCd or VRLA)

- Cells in series

- Number of battery sets/strings

- Battery enclosure rating (NEMA/IP)

- Required backup/autonomy (hours @ C-rate)

D. Panel Board / LOS / DB

- Whether LOS/DB exists

- Enclosure rating (NEMA-4/X etc.)

- Exact breaker count & ratings

  - Example:

    - 1 × 100AF/100AT

    - 10 × 100AF/30AT

    - 4 × 100AF/20AT

    - 4 spaces

2. List the following separately (NOT inside the table):

A. Relevant Notes per Equipment

List all note numbers or text exactly as shown for:

- PV/charge controller

- Batteries

- LOS/DB/DC panels

B. Additional Equipment Not Covered in the Table

List everything else present on SLD such as:

- RTU

- Lighting control panel

- HOV loads

- Surge relief skid

- Photo cell

- Outdoor lights

- Communication devices

- Spare feeders

- Cable tags

C. Critical Design Considerations

Always include:

- 120 hours (5-day) autonomy if shown

- Equipment must be installed outside classified area

- All alarms/signals must go to RTU (hard-wired + Ethernet)

- Ambient temperature derating for MCCBs/controllers

- Mandatory fused combiner before MPPT controller

- Compliance with SAES/SAMSS

- Standards cutoff date (if shown)

3. Rules

- Do not assume anything.

- If terminology varies (e.g., “PV JB” vs “combiner box”), highlight variation.

- If any field is unclear → “Not stated in SLD.”

- Do not treat LCD/internal display alarms as hard-wired signals.

- Only report what is explicitly drawn or written.

- Try to read the document zoomed-in, the text might be jumbled up if you’re not zooming in.

Response from ChatGPT:

1.a) A. Solar Panels / PV

| Field | System 1 |
| --- | --- |
| Solar configuration (1×100% or 2×50%) | Not stated in SLD. (Note-11 says vendor shall confirm number of PV arrays and arrangement.) |
| PV Array Junction Box required? | Yes. “JUNCTION BOX PHOTOVOLTAIC ARRAY (24VDC) ENCLOSURE NEMA-4X” is shown between PV array and charger. |
| Charge controller type (MPPT / PWM) | MPPT. Note-14: “FUSED DISCONNECT COMBINER BETWEEN PHOTOVOLTAIC (SOLAR) SYSTEM ARRAYS AND MPPT CHARGE CONTROLLER SHALL BE PROVIDED BY VENDOR.” |

1.b) B. Charge Controller → RTU

| Field | System 1 |
| --- | --- |
| Hard-wired signals from controller to RTU (LCD/internal alarms excluded) | Under “STATUS ALARM SIGNALS TO RTU (HARDWIRED)” the following are listed: • ALARM FROM CONTROLLER A/B • BATTERY BANK A/B VOLTAGE LOW ALARM • CHARGER FAULT AND COMMON • BATTERY MCCB OPEN • LOW BATTERY STATE OF CHARGE • LOAD DISCONNECTED |
| Ethernet cable drawn between controller and RTU? | Yes. “ETHERNET CABLE (BY I&C)” is shown between controller and RTU. |

1.c) C. Battery System

| Field | System 1 |
| --- | --- |
| Battery breaker box required? | Yes. A “BREAKER IN NEMA-4X ENCLOSED CIRCUIT (SEE NOTE 13)” is shown adjacent to the stationary battery, plus tag “2P 400A (VENDOR SUPPLY)”. |
| Number of battery breaker boxes | 1 NEMA-4X enclosed breaker box is shown on the battery side. |
| Battery configuration (1×100% or 2×50%) | Not stated in SLD. Only “1400 Ah (4 SETS)” is shown; no explicit 1×100% / 2×50% wording. |
| Battery type | Ni-Cd. Text: “19 CELLS Ni-Cd BATTERIES”. |
| Cells in series | 19 cells in series. |
| Number of battery sets / strings | 4 sets (“1400 Ah (4 SETS)”). |
| Battery enclosure rating | NEMA 4 ENCLOSURE is written under “STATIONARY BATTERY K18-(SP-001)-SB-0001”. |
| Required backup / autonomy | “@ C5, 120 HOURS BACK UP 1400 Ah (4 SETS)” – i.e. 120-hour autonomy at C5 rate. |

1.d) D. Panel Board / LOS / DB (24VDC Power Panel)

| Field | System 1 |
| --- | --- |
| Whether LOS/DB exists | Yes. “K18-(SP-001)-PP-0001, 24VDC POWER PANEL” is shown (location: outdoor). |
| Enclosure rating | NEMA-4X is explicitly indicated for this panel. |
| Exact breaker count & ratings (panelboard itself) | From the panel schedule section: • Bus: “100A, 24VDC BUS, 10kAIC, 1 SEC” • Main breaker: 1 × 2P 100AF / 100AT • Branch breakers (all 2-pole, 100AF frame): – 13 × 30AT (2P 100AF/30AT) – these include feeders to RTU, comms, lights, HOV loads and some spares. – 4 × 20AT (2P 100AF/20AT) • Spaces: text “SPACE SPACE” appears once under the panel, indicating 2 unused ways. • Spare feeders: “SPARE SPARE SPARE” loads are indicated; ratings correspond to some of the 30AT feeders but are not separately labelled, so individual spare ratings per circuit are not stated in SLD. |

- Items requested outside the table

2.a) Relevant notes per equipment

(Notes are copied as literally as possible from the SLD.)

a. PV / Charge controller

- Note-11 – “VENDOR SHALL CONFIRM THE NUMBER OF PHOTOVOLTAIC (SOLAR) SYSTEM ARRAY AND INSTALLATION ARRANGEMENT, JUNCTION BOXES.”

- Note-13 – “VENDOR SHALL CONFIRM THE RATINGS OF PHOTOVOLTAIC (SOLAR) SYSTEM CHARGER CONTROLLER AND CIRCUIT BREAKERS.”

- Note-14 – “FUSED DISCONNECT COMBINER BETWEEN PHOTOVOLTAIC (SOLAR) SYSTEM ARRAYS AND MPPT CHARGE CONTROLLER SHALL BE PROVIDED BY VENDOR.”

b. Batteries

- Note-2 – “VENDOR SHALL PROVIDE BATTERY IN ACCORDANCE WITH 17-SAMSS-511, AND LATEST EDITION OF NFPA-70.”

- Note-3 – “OUTDOOR BATTERY INSTALLATIONS, BATTERY ENCLOSURE SHALL BE MADE NON-METALLIC (MADE OF FIBERGLASS REINFORCED) MATERIAL AS PER SAES-P-128.”

- Note-12 – “VENDOR SHALL CONFIRM THE BATTERY Ah CAPACITY.”

- The battery block itself states: “STATIONARY BATTERY K18-(SP-001)-SB-0001 NEMA 4 ENCLOSURE 19 CELLS Ni-Cd BATTERIES 1400 Ah (4 SETS) @ C5, 120 HOURS BACK UP (SEE NOTE-12).”

- The adjacent breaker box states: “BREAKER IN NEMA-4X ENCLOSED CIRCUIT (SEE NOTE 13).”

c. LOS / DB / DC panels

For the 24VDC power panel K18-(SP-001)-PP-0001 and associated DC bus:

- Note-4 – “VENDOR SHALL CONSIDER SITE DERATING FOR AMBIENT TEMPERATURES IN THE SELECTION OF BREAKERS (MCCB) AS PER TABLE-1 OF SAES-A-112, TABLE-1 (40°C).”

- Note-5 – “ALL ALARM INDICATIONS AND INSTRUMENTATION SHALL BE IN ACCORDANCE WITH SAES-P-103, AND 17-SAMSS-514.”

- Note-6 – “THE LV PANELBOARD SHALL BE MANUFACTURED IN ACCORDANCE WITH 16-SAMSS-518.”

- Note-7 – “DC BUS SHALL BE MANUFACTURED IN ACCORDANCE WITH APPLICABLE SAUDI ARAMCO MANUFACTURING SPECIFICATION (SAMS).”

- Note-9 – “ALL PANEL BOARD SHALL BE TOTALLY ENCLOSED DEAD FRONT CIRCUIT TYPE. MULTI-POLE BREAKERS SHALL HAVE COMMON TRIP AND SINGLE OPERATING HANDLE.”

- Panel label: “K18-(SP-001)-PP-0001, 24VDC POWER PANEL (NEMA-4X) LOCATION: OUTDOOR 100A, 24VDC BUS, 10kAIC, 1 SEC.”

2.b) Additional equipment not covered in the table

Everything below is explicitly shown somewhere on the SLD:

- RTU and interfaces

  - “K18-RTU-740 RTU FEEDER-1 (400 WATTS) COMMUNICATION EQUIPMENT FEEDER-1”.

  - “K18-RTU-740 RTU FEEDER-2 (400 WATTS) (BACK-UP) COMMUNICATION EQUIPMENT FEEDER-2 (400 WATTS) (BACK-UP)”.

  - “RTU REMOTE TERMINAL UNIT” symbol in the legend.

  - “STATUS ALARM SIGNALS TO RTU (HARDWIRED)” plus “ETHERNET CABLE (BY I&C)” shown between charger and RTU.

- Lighting system

  - “LIGHTING CONTROL PANEL K18-(SP-001)-CP-0001 (LOCATED NEXT TO DC POWER PANEL) (SEE NOTE-2 & 3).”

  - “LIGHTING CONTACTOR PANEL” with schematic labelled “LIGHTING CONTACTOR SCHEMATIC DIAGRAM”.

  - Elements in that schematic: “HAND / OFF / AUTO” selector switch, “FUSE 10A”, “PC” (photo cell) symbol, contactor coil “C”, and “OUTDOOR TYPE LIGHT CIRCUIT 9,11”.

  - “LIGHTING SHELTER (50 WATTS)” connected to one of the DC panel circuits.

- HOV loads

  - “K18-HOV-00770 (500 WATTS)”

  - “K18-HOV-00771 (500 WATTS)”

  - “K18-HOV-00772 (500 WATTS)”

- Other DC panels / loads

  - “DC POWER PANEL K18-PC-3926 (PANEL INSIDE SHELTER) (LOCATED NEXT TO DC POWER PANEL)”

  - Additional loads/feeder tags: “K18-PC-3921”, “K18-PC-3922”, “K18-PC-3923”, “K18-PC-3924”, “K18-PC-3925”, “K18-PC-3927”, “K18-PC-3928”, “K18-PC-3929”.

  - Some feeder destinations are marked as “SPARE SPARE SPARE”.

- Cabling / tags

  - Under cable legend: “POWER CABLE TAG NUMBER K18-PC-XXXX SEQUENCE NUMBER CABLE MARKING PLANT NUMBER”.

- PV & associated items (not already in table)

  - Legend items: “PHOTOVOLTAIC (SOLAR) PANELS”, “JUNCTION BOX NEMA-4 PHOTOVOLTAIC ARRAY (-) (+)”.

  - Earthing symbol “EARTH” (for system grounding).

- Miscellaneous

  - General title block: “MLIV STATION @ KM. 3.40 EAST/WEST PIPELINE #2 YANBU K18”.

  - Reference drawings: cable routing layout, cable and conduit schedule, panel schedule, lighting layout, etc.

2.c) Critical Design Considerations

(Each item below is checked against the SLD; if it is not clearly present, it is marked “Not stated in SLD.”)

- 120 hours (5-day) autonomy

  - Explicitly shown: “@ C5, 120 HOURS BACK UP 1400 Ah (4 SETS) 19 CELLS Ni-Cd BATTERIES” under the stationary battery.

- Equipment must be installed outside classified area

  - Note-8: “PHOTOVOLTAIC (SOLAR) SYSTEM EQUIPMENT SHALL NOT BE INSTALLED/LOCATED INSIDE THE CLASSIFIED AREA.”

- All alarms/signals must go to RTU (hard-wired + Ethernet)

  - The drawing shows “STATUS ALARM SIGNALS TO RTU (HARDWIRED)” and an “ETHERNET CABLE (BY I&C)” between charger and RTU.

  - Note-5 ties alarm indications & instrumentation to SAES/ SAMSS, but it does not explicitly say “all alarms must go to RTU”; that requirement is only implied by the connections. So stricter statement “all alarms/signals must go to RTU” is not explicitly written; only the specific list of hard-wired alarms plus Ethernet link are shown.

- Ambient temperature derating for MCCBs/controllers

  - Note-4: “VENDOR SHALL CONSIDER SITE DERATING FOR AMBIENT TEMPERATURES IN THE SELECTION OF BREAKERS (MCCB) AS PER TABLE-1 OF SAES-A-112, TABLE-1 (40°C).”

  - No explicit derating text for the charge controller itself beyond this breaker note.

- Mandatory fused combiner before MPPT controller

  - Note-14 (quoted above) explicitly requires a “FUSED DISCONNECT COMBINER BETWEEN PHOTOVOLTAIC (SOLAR) SYSTEM ARRAYS AND MPPT CHARGE CONTROLLER”.

- Compliance with SAES / SAMSS

  - Note-1: “PHOTOVOLTAIC (SOLAR) SYSTEM AND INSTALLATION SPECIFICATION SHALL BE IN ACCORDANCE WITH SAUDI ARAMCO ENGINEERING STANDARD SAES-P-103 AND SAES-P-128.”

  - Note-2: batteries to be in accordance with 17-SAMSS-511 and NFPA-70.

  - Note-5, Note-6, Note-7 also reference SAES-P-103, 17-SAMSS-514, 16-SAMSS-518 and SAMS for DC bus/panelboard and instrumentation.

- Standards cutoff date (if shown)

  - Note-15: “SAUDI ARAMCO STANDARDS, CUT-OFF DATE MAY 2023 SHALL BE PROVIDED BY VENDOR.”

- Terminology variations (as requested)

  - The PV junction box is labelled as “JUNCTION BOX PHOTOVOLTAIC ARRAY (24VDC) ENCLOSURE NEMA-4X” rather than “PV JB”.

  - The combiner is only mentioned in Note-14 as “FUSED DISCONNECT COMBINER”; there is no separate graphic symbol explicitly tagged “COMBINER BOX” or “PV JB” on the line, so the terminology switches between “JUNCTION BOX” on the single-line and “FUSED DISCONNECT COMBINER” in the notes.