## SLD Data
Item / Question | MLIV STATION @ KM.19.400 K18-(SP-002) | Site 2 | Site 3
Solar panels configuration? 1×100% or 2×50%? | Not stated
Array Junction Boxes required? | Yes - JUNCTION BOX PHOTOVOLTAIC ARRAY (24VDC) ENCLOSURE NEMA-4X
Charge controller type? MPPT or PWM? | MPPT - Note-14 references MPPT CHARGE CONTROLLER
List of hard-wired signals from charge controller to RTU
Any other signals/alarms from charge controller? | Ethernet cable shown between controller and RTU
Battery breaker box required? | Yes
No. of battery breaker boxes required? | Yes
Battery configuration? 1×100% or 2×50%? | Not stated - shows 325 Ah (1 SETS)
Battery type? NiCd or VRLA? | NiCd
How many cells in series? | 19
How many strings / sets of batteries?
Required battery enclosure IP / NEMA rating?
Required back-up / autonomy?
Panel board / DB / LOS required?
Enclosure rating of LOS / power panel?
Number of breakers and ratings in LOS?
Relevant notes for PV / charge controller?
Relevant notes for batteries / enclosure?
Other equipment not explicitly covered? | RTU feeders (K18-U-0004), HOV loads (K18-HOV-00773 through K18-HOV-00824 at 500W each), Surge relief skid, DIT equipment (K18-DIT-00912 at 30W), spare circuits
Any other critical points for system design? | 120-hour autonomy required, equipment not to be installed in classified area per Note-8, ambient temperature derating per Note-4 (40°C), compliance with SAES-P-103/SAES-P-128 and various SAMSS standards, Saudi Aramco standards cutoff date May 2023