## SLD Data
Item / Question | K18-(SP-002) MLIV Station @ KM.19.400 | Site 2 | Site 3
Solar panels configuration? 1×100% or 2×50%? | Not stated
Array Junction Boxes required? | Yes - JUNCTION BOX PHOTOVOLTAIC ARRAY (24VDC) ENCLOSURE NEMA-4X
Charge controller type? MPPT or PWM? | MPPT - SOLAR CHARGER CONTROLLER 30AMP
List of hard-wired signals from charge controller to RTU
Any other signals/alarms from charge controller? | Ethernet cable connection to RTU, LCD display alarms (internal only)
Battery breaker box required? | Yes
No. of battery breaker boxes required? | Yes
Battery configuration? 1×100% or 2×50%? | Not stated - shows 1 SETS configuration
Battery type? NiCd or VRLA? | Ni-Cd
How many cells in series? | 19
How many strings / sets of batteries?
Required battery enclosure IP / NEMA rating?
Required back-up / autonomy?
Panel board / DB / LOS required?
Enclosure rating of LOS / power panel?
Number of breakers and ratings in LOS?
Relevant notes for PV / charge controller?
Relevant notes for batteries / enclosure?
Other equipment not explicitly covered? | RTU feeders (K18-RTU-740), HOV loads (K18-HOV-00773 through 00824, 500W each), DIT equipment (K18-DIT-00912, 30W), Surge relief skid (K18-U-0004)
Any other critical points for system design? | 120-hour autonomy required, Equipment not in classified area per Note-8, Ambient temperature derating per Note-4 (40°C), Saudi Aramco standards cutoff May 2023, All alarms to RTU via hardwired and Ethernet