## SLD Data
Item / Question | MLIV Station @ KM. 3.40 East/West Pipeline #2 Yanbu K18 | Site 2 | Site 3
Solar panels configuration? 1×100% or 2×50%? | Not stated in SLD. Note-11 says vendor shall confirm number of PV arrays and arrangement
Array Junction Boxes required? | Yes. Junction Box Photovoltaic Array (24VDC) Enclosure NEMA-4X is shown between PV array and charger
Charge controller type? MPPT or PWM? | MPPT. Note-14 references MPPT charge controller and requires fused disconnect combiner
List of hard-wired signals from charge controller to RTU
Any other signals/alarms from charge controller? | Ethernet cable (By I&C) shown between controller and RTU
Battery breaker box required? | Yes. Breaker in NEMA-4X Enclosed Circuit is shown
No. of battery breaker boxes required? | Yes. Breaker in NEMA-4X Enclosed Circuit is shown
Battery configuration? 1×100% or 2×50%? | Not explicitly stated. Shows 1400 Ah (4 SETS)
Battery type? NiCd or VRLA? | NiCd
How many cells in series? | 19 cells
How many strings / sets of batteries?
Required battery enclosure IP / NEMA rating?
Required back-up / autonomy?
Panel board / DB / LOS required?
Enclosure rating of LOS / power panel?
Number of breakers and ratings in LOS?
Relevant notes for PV / charge controller?
Relevant notes for batteries / enclosure?
Other equipment not explicitly covered? | RTU (K18-RTU-740), Lighting Control Panel K18-(SP-001)-CP-0001, DC Power Panel K18-PC-3926, HOV loads (K18-HOV-00770/771/772 at 500W each), Photo cell, Outdoor lights, Communication equipment feeders
Any other critical points for system design? | 120 hours (5-day) autonomy required. Equipment shall not be installed inside classified area per Note-8. Ambient temperature derating for MCCBs per Note-4 (40°C). Mandatory fused combiner before MPPT controller per Note-14. Compliance with SAES-P-103, SAES-P-128, 17-SAMSS-511, and other SAES/SAMSS standards. Saudi Aramco standards cut-off date May 2023 per Note-15