## SLD Data
Item / Question | MLIV STATION @ KM. 34.00 EAST/WEST PIPELINE #2 YANBU K18 | Site 2 | Site 3
Solar panels configuration? 1×100% or 2×50%? | Not stated
Array Junction Boxes required? | Yes - JUNCTION BOX PHOTOVOLTAIC ARRAY (24VDC) ENCLOSURE NEMA-4X shown between PV array and charger
Charge controller type? MPPT or PWM? | MPPT - Note-14 references MPPT CHARGE CONTROLLER
List of hard-wired signals from charge controller to RTU
Any other signals/alarms from charge controller? | ETHERNET CABLE (BY I&C) shown between controller and RTU
Battery breaker box required? | Yes
No. of battery breaker boxes required? | Yes
Battery configuration? 1×100% or 2×50%? | Not stated - only shows 1400 Ah (4 SETS)
Battery type? NiCd or VRLA? | NiCd
How many cells in series? | 19
How many strings / sets of batteries?
Required battery enclosure IP / NEMA rating?
Required back-up / autonomy?
Panel board / DB / LOS required?
Enclosure rating of LOS / power panel?
Number of breakers and ratings in LOS?
Relevant notes for PV / charge controller?
Relevant notes for batteries / enclosure?
Other equipment not explicitly covered? | RTU K18-RTU-750 with dual feeders (400W each), LIGHTING CONTROL PANEL K18-(SP-003)-CP-0001, HOV loads K18-HOV-00776/777/778 (500W each), DC POWER PANEL inside shelter, Photo cell for lighting control, Outdoor type light circuits
Any other critical points for system design? | 120 hours (5-day) autonomy required, Equipment shall not be installed inside classified area per Note-8, Ambient temperature derating for breakers per Note-4 (40°C), Fused disconnect combiner mandatory before MPPT controller per Note-14, Compliance with SAES-P-103, SAES-P-128, 17-SAMSS-511, 16-SAMSS-518, Standards cutoff date MAY 2023 per Note-15