## Sheet1
Solar Panels Configuration? 1x100% or 2x50%?
Charge Controllers Configuration? 1x100% or 2x50%?
Batteries Configuration? 1x100% or 2x50%?
Load-list of each site? Mention the run-time of each load.
Future expansion factor considered in Battery Calculations?
Battery back-up time?
Ageing factor for Battery?
Design factor for Battery?
Temperature compensation for battery?
Any other factor client considered for battery? What is its value? List down all the factors and their values one by one
Computed Required battery Capacity calculated by the client?
End of Discharge voltage per cell?
Number of cells in series?
Proposed Battery cell capacity?
Number of parallel sets/strings as per the client?
List down all the derating factors in bullets, client considered for Solar Array Calculation. Also mention their respective values.
Sun hours considered?
Any future factor considered in the load current of solar section? Or is the load current considered in Solar Array section is the same as that of Load current + Future in the battery section?
Mention the formula client has considered to size the solar array
How many solar panels in one string?
How many parallel solar panels?
Responses from ChatGPT
Item / Question | MLIV-1 @ KM 3.40 (SP-001) | MLIV-2 @ KM 19.40 (SP-002) | MLIV-3 @ KM 34.00 (SP-003)
Solar Panels Configuration? 1x100% or 2x50%? | 1x100% | 1x100% | 1x100%
Charge Controllers Configuration? 1x100% or 2x50%? | 1x100% | 1x100% | 1x100%
Batteries Configuration? 1x100% or 2x50%? | 1x100% | 1x100% | 1x100%
Load-list of each site? Mention the run-time of each load. | 1- K18-RTU-740 (400W, 24hrs), 2- HOV (1500W, 0.16hrs), 3- RTU CABINET LTG. (50W, 5hrs) | K18-RTU-750 (400W, 24hrs), HOV (1500W, 0.16hrs), RTU CABINET LTG. (50W, 5hrs) | K18-DIT-00912 (30W, 720hrs), K18-U-0004 Surge relief Skid (50W, 0.25hrs), HOV (2500W, 0.16hrs)
Future expansion factor considered in Battery Calculations? | 1.1 (10%) | 1.1 (10%) | 1.1 (10%)
Battery back-up time? | 120 hours | 120 hours | 120 hours
Ageing factor for Battery? | 1.25 | 1.25 | 1.25
Design factor for Battery? | 1.1 | 1.1 | 1.1
Temperature compensation for battery? | 1 (Ni-Cd) | 1 (Ni-Cd) | 1 (Ni-Cd)
Any other factor client considered for battery? What is its value? List down all the factors and their values only one | Battery Capacity @ C120: 1400 Ah (4 parallel sets); @ C5: 1400 Ah | Battery Capacity @ C120: 1400 Ah (4 parallel sets); @ C5: 1400 Ah | Battery Capacity @ C120: 325 Ah (1 parallel set); @ C5: 325 Ah
Computed Required battery Capacity calculated by the client? | 6440 Ah @ C120 | 6440 Ah @ C120 | 373.75 Ah @ C120
End of Discharge voltage per cell? | 1.2 VPC | 1.2 VPC | 1.2 VPC
Number of cells in series? | 19 | 19 | 19
Proposed Battery cell capacity? | 1400 Ah (@ C5, 4 parallel sets) | 1400 Ah (@ C5, 4 parallel sets) | 325 Ah (@ C5, 1 parallel set)
Number of parallel sets/strings as per the client? | 4 parallel sets | 4 parallel sets | 1 parallel set
List down all the derating factors in bullets, client considered for Solar Array Calculation. Also mention their respective values. | - Dust Factor: 1.2 | - Dust Factor: 1.2 | - Dust Factor: 1.2
| - Aging Factor: 1.1 | - Aging Factor: 1.1 | - Aging Factor: 1.1
| - Future Expansion Factor: 1.1 | - Future Expansion Factor: 1.1 | - Future Expansion Factor: 1.1
Sun hours considered? | 5 effective sun hours | 5 effective sun hours | 5 effective sun hours
Any future factor considered in the load current of solar section? Or is the load current considered in Solar Array section is the same as that of Load current + Future in the battery section? | Load Current (A): 34.18; Load Current + Future: 37.60 A (includes 1.1 future factor) | Load Current (A): 34.18; Load Current + Future: 37.60 A (includes 1.1 future factor) | Load Current (A): 1.97; Load Current + Future: 2.16 A (includes 1.1 future factor)
Mention the formula client has considered to size the solar array | Per SAES-P-128 Attachment-1: Array sized to recharge battery to 95% in 30 days, based on 5 effective sun hours, de-rated 10% for aging, 20% for dust accumulation, and 10% for future growth | Per SAES-P-128 Attachment-1: Array sized to recharge battery to 95% in 30 days, based on 5 effective sun hours, de-rated 10% for aging, 20% for dust accumulation, and 10% for future growth | Per SAES-P-128 Attachment-1: Array sized to recharge battery to 95% in 30 days, based on 5 effective sun hours, de-rated 10% for aging, 20% for dust accumulation, and 10% for future growth
Total Daily Required Ah (Solar Array Section)? | 1547.4 Ah | 1547.4 Ah | 89.111 Ah
How many solar panels in one string? | Not explicitly stated in document | Not explicitly stated in document | Not explicitly stated in document
How many parallel solar panels? | 30 parallel modules | 30 parallel modules | 2 parallel modules