## Sizing Data
Item / Question | MLIV-1 AT KM 3.40 | MLIV-3 AT KM 34.00 | MLIV-2 AT KM 19.400
Solar Panels Configuration? 1x100% or 2x50%? | 1x100% | 1x100% | 1x100%
Charge Controllers Configuration? 1x100% or 2x50%? | 1x100% | 1x100% | 1x100%
Batteries Configuration? 1x100% or 2x50%? | 1x100% | 1x100% | 1x100%
Load-list of each site? Mention the loads, power & operating hours | Communication Equip. (400W, 24V, 16.67A, 24hrs, 9600Wh/day), RTU CABINET LTG. (50W, 24V, 2.08A, 5hrs, 250Wh/day), HOV (1500W, 24V, 62.50A, 0.16hrs, 240Wh/day) | Communication Equip. (400W, 24V, 16.67A, 24hrs, 9600Wh/day), RTU CABINET LTG. (50W, 24V, 2.08A, 5hrs, 250Wh/day), HOV (1500W, 24V, 62.50A, 0.16hrs, 240Wh/day) | K18-DIT-00912 (30W, 24V, 1.25A, 24hrs, 720Wh/day), K18-U-0004 Surge relief Skid (50W, 24V, 2.08A, 0.25hrs, 12.5Wh/day), HOV (2500W, 24V, 104.17A, 0.16hrs, 400Wh/day)
Future expansion factor considered in Battery calculation? | 1.1 (10%) | 1.1 (10%) | 1.1 (10%)
Battery back-up time?
Ageing factor for Battery? | 1.25 | 1.25 | 1.25
Design factor for Battery? | 1.1 | 1.1 | 1.1
Temperature compensation for battery? | 1 (for Ni-Cd) | 1 (for Ni-Cd) | 1 (for Ni-Cd)
Any other factor client considered for Battery Capacity? | 6204.4 Amp Hour at C120 | 6204.4 Amp Hour at C120 | 356.9 Amp Hour at C120
Computed Required battery Capacity at the end? | 6204.4 Amp Hour at C120 | 6204.4 Amp Hour at C120 | 356.9 Amp Hour at C120
End of Discharge voltage per cell? | 1.2 VPC | 1.2 VPC | 1.2 VPC
Number of cells in series? | 19 | 19 | 19
Proposed Battery cell capacity?
Number of parallel sets/strings as per proposal?
List down all the derating factors for Solar Sizing? | Aging Factor: 1.1, Dust Factor: 1.2 | Aging Factor: 1.1, Dust Factor: 1.2 | Aging Factor: 1.1, Dust Factor: 1.2
Sun hours considered? | 5 effective sun hours | 5 effective sun hours | 5 effective sun hours
Any future factor considered in the Solar Sizing?
Mention the formula client has considered for Solar Sizing
Total Daily Required Ah (Solar Array sizing)?
How many solar panels in one string?
How many parallel solar panels? | 30 parallel modules | 30 parallel modules | 2 parallel modules